# General

Air Handling Units shall be manufactured in Australia by Armcor Air Solutions www.armcor.com.au  Ph.  1800   244   556. The units shall be factory assembled and internally wired, and fitted with large access doors allowing for service, cleaning and maintenance. The unit shall comply with the following design and manufacturing  requirements and comply with the capacity requirement outlined in the attached performance schedule.

The manufacturer shall undertake a pre–commissioning check to ensure correct operation before the equipment leaves the factory.

Equipment shall be installed in a manner strictly in accordance with the manufacturers’ recommendations.

# Unit Construction

The unit shall be completely weatherproof and constructed according to the following requirements:

- The unit shall have a rigid galvanised steel base frame with crane lifting points.

- The unit casing shall be constructed from 50mm double skin insulated Colorbond® panel.

- The external panel shall have a minimum thermal rating of R1.5

- Units shall have large access doors to allow the internal parts to be accessed easily and removed for cleaning, servicing, maintenance, repair or replacement.

- Access doors shall be hinged and fitted with easy access opening mechanism.

- Access doors shall be fitted with rubber seals to eliminated air leakage.

- Powdercoated aluminum profiles shall be used to join the casing panels, including H section, U section, base channel, door stop and angles.

- All panels are to be fully sealed with non-perishable, mildew and mould resistant sealant and shall contain a VOC rating designed for extreme weather conditions.

# Fans

# OPTION A [for EC Plug Fan Application]

Fans used in the equipment shall be:

- Direct drive EC Backward Curved Centrifugal Plug Fans with Soft Start

- 0 – 10 Volt control input, to suit Variable Speed Drive (VSD) controller

- Thermal overload motor protection

- Performance to meet the required airflows and static pressures

# OPTION B [for multi speed Centrifugal Fan Application]

Fans used in the equipment shall be:

- Direct drive Forward Curved Centrifugal Fans

- Multi speed control

- Thermal overload motor protection

- Performance to meet the required airflows and static pressures

# Electrical

The unit is to be fully factory wired with a control box for site connection. Electrical cables shall be run neatly and in cable ducts. All wiring shall be independently colour coded. Circuit breakers, contactors and overloads shall be fitted for all three phase motors.

The following components shall also be incorporated and factory fitted:

[Select the appropriate options if required]

- Integrated Variable Speed Drive (VSD) controller

- 24 volt/240 volt contactors

# Coils (detail coil requirements)

Hot Water /Chilled Water Coils shall be constructed from copper tubes with bonded aluminium fins and have the following features:

- The velocity through the coils shall be designed at a maximum of 2.3 m/sec for low pressure drop and high efficiency

- Coils shall be pressure tested to 2200kPa (22 bar)

- The coils shall meet the required capacities outlined in the performance schedule

- Where cooling coils are included a stainless-steel drain tray shall be installed to capture any condensation

# Filters (if required)

Filters shall be incorporated into the unit casing or as a separate matching module. Filters shall be easily removable through an access door for cleaning and replacement.

Filters shall be: [select option]

- 50mm V form disposable panel filters with F4 media.

- 600 deep bag filters.

- Dual filters - 600 deep bag filters and 50mm V form disposable panel pre-filters

# Performance Schedule

| Unit Ref | Fan Capacity | Coil Capacity | Model | Comments |
| --- | --- | --- | --- | --- |
|  | S/A (I/s) | O/A (I/s) | Ext Strat (Pa) | Fan Type | Cooling | Heating |  |  |
| Example | 1200 | 300 | 200 | EC Plug | 27kW Chilled Water | 20kW Hot Water | AHU1200AF | 50mm Panel Filters in Unit |