# General

Ceiling Mounted Energy Recovery equipment shall be manufactured in Australia by Armcor Air Solutions www.armcor.com.au Ph. 1800 244 556. The units shall be factory assembled and internally wired, and fitted with large access doors allowing for service, cleaning, and maintenance. The unit shall comply with the following design and manufacturing requirements and comply with the capacity requirement outlined in the attached performance schedule.

The manufacturer shall undertake a pre–commissioning check to ensure correct operation before the equipment leaves the factory.

Equipment shall be installed in a manner strictly in accordance with the manufacturers’ recommendations.

# Unit Construction

The unit shall be constructed according to the following requirements:

- The unit casing shall be constructed from heavy duty galvanised steel with a minimum thickness of 1.0 mm

- Thermal internal insulation shall be used, having a density of not less than 36kg/m³, and a minimum thermal rating of R1.5

- Units shall have large access doors to allow the internal parts to be accessed easily and removed for cleaning, servicing, maintenance, repair, or replacement.

- Units shall incorporate accessible filters in both the fresh air intake and return air intake.

- Units to have multi directional inlet and outlet locations to provide ease of onsite installation.

# Heat Exchanger

# OPTION A [for Sensible Energy Recovery Applications]

The heat exchanger shall be a Sensible plate heat exchanger with the following features:

- Sized to meet the required performance specifications.

- Incorporate no moving parts.

- Have entirely separate air paths for the supply and exhaust air to ensure no cross contamination

- Heat exchanger frame shall be formed from min 0.6mm coated steel or stabilized UPVC

# OPTION B [for Enthalpy Energy Recovery Applications]

The heat exchanger shall be an Enthalpy plate heat exchanger with the following features:

- Sized to meet the required performance specifications.

- Incorporate no moving parts.

- Heat exchanger frame shall be formed from min 0.6mm coated steel or stabilized UPVC

# Fans

# OPTION A [for EC Plug Fan Application]

Fans used in the equipment shall be:

- Direct drive EC Backward Curved Centrifugal Plug Fans with Soft Start

- 0 – 10 Volt control input, to suit Variable Speed Drive (VSD) controller

- Thermal overload motor protection

- Performance to meet the required airflows and static pressures

# OPTION B [for multi speed Centrifugal Fan Application]

Fans used in the equipment shall be:

- Direct drive Forward Curved Centrifugal Fans

- Multi speed control

- Thermal overload motor protection

- Performance to meet the required airflows and static pressures

# Filters

Filters shall be incorporated into the unit casing and shall be easily removable through the access doors for cleaning and replacement.

Filters shall be:

- 10 mm panel filters with washable media (less than 200l/sec capacity)

- 50mm V form disposable panel filters with F4 media (greater than 200l/sec capacity)

# Electrical

The unit is to be fully factory wired with a terminal box or lead & plug for site connection.

[Select this option for EC Plug fans]

A factory fitted Integrated Variable Speed Drive (VSD) controller shall be included.

# Performance Schedule

| Unit Ref | Air Flow Capacity | Heat Exchanger Capacity | Fan Type | Model | Comments |
| --- | --- | --- | --- | --- | --- |
|  | S/A (I/s) | O/A (I/s) | Ext Strat (Pa) | Type | Kw Recovered (Cool) | Kw Recovered (Heat) |  |  |  |
| Example | 425 | 425 | 200 | Plate | 5.79 | 7.43 | EC Plug | XCM425 | 50mm Filter Included |