# General

Humidity & Temperature Control (HTC) equipment shall be manufactured in Australia by Armcor Air Solutions www.armcor.com.au Ph. 1800 244 556. The units shall be factory assembled and internally wired, and fitted with large access doors allowing for service, cleaning and maintenance. The unit shall comply with the following design and manufacturing requirements and comply with the capacity requirement outlined in the attached performance schedule.

The manufacturer shall undertake a pre–commissioning check to ensure correct operation before the equipment leaves the factory.

Equipment shall be installed in a manner strictly in accordance with the manufacturers’ recommendations.

# Unit Construction

The unit shall be completely weatherproof and constructed according to the following requirements:

- The unit shall have a rigid galvanised steel base frame with crane lifting points

- The unit casing shall be constructed from 50mm double skin insulated Colorbond® panel

- The external panel shall have a minimum thermal rating of R1.5

- Units shall have large access doors to allow the internal parts to be accessed easily and removed for cleaning, servicing, maintenance, repair or replacement.

- Access doors shall be hinged and fitted with easy access opening mechanism.

- Access doors shall be fitted with rubber seals to eliminated air leakage

- Powdercoated aluminium profiles shall be used to join the casing panels, including H section, U section, base channel, door stop and angles

- All panels are to be fully sealed with non-perishable, mildew and mould resistant sealant and shall contain a VOC rating designed for extreme weather conditions

- A stainless steel drain tray shall be installed to capture any condensation

# Air-conditioning System

The equipment shall include compressors, coils, refrigeration pipework and controls to effect the necessary dehumidification and/or cooling specifications. Gas shall be R407C suitable for high ambient conditions.

# Evaporator coils and condenser coils

- The velocity through the coils shall be designed at a maximum of 2.3 m/sec for low pressure drop and high efficiency

- Coils shall be pressure tested to 2200kPa (22 bar)

- The coils shall meet the required capacities outlined in the performance schedule

# Refrigeration pipework

- Sized to suit the unit capacity and supported to minimize vibration

- Reversing valves, pressure sensors and associated components shall be professionally factory installed

- Complete system to be pressure tested to a min of 2200pa, vacuumed to 50 microns and charged with the correct refrigerant

- System commission and check

- System to be factory run for a min of 2 hours and be fully factory commissioned

# Reheat System

The equipment shall include a hot water reheat coil ready for connection to an external hot water source.

- The velocity through the coils shall be designed at a maximum of 2.3/sec for low pressure drop and high efficiency

- Coils shall be pressure tested to 2200kPa (22 bar)

- The coils shall meet the required capacities outlined in the performance schedule

# Fans

Fans used in the equipment shall be:

- Direct drive EC Backward Curve Plug Fans with Soft Start

- 0 – 10 Volt control input

- Thermal overload and phase protection

- Performance to meet the required airflows and static pressures

- Fault output relay

# Heat Exchanger [if required]

The heat exchange module shall be a Sensible plate heat exchanger with the following features:

- Crossflow or Counterflow Design so as to meet the required specifications

- Incorporate no moving parts

- Have entirely separate air paths for the supply and exhaust air to ensure no cross contamination

- Heat exchanger frame shall be formed from min 0.6mm coated steel or stabilized UPVC

# Filters [if required]

Filters shall be incorporated into the unit casing or as a separate matching module. Filters shall be easily removable through an access door for cleaning and replacement.

Filters shall be: [select option]

- 50mm V form disposable panel filters with F4 media

- F5 bag filters

- Dual filters bag filters and 50mm V form disposable panel pre-filters

# Electrical

The unit is to be fully factory wired with a control box for site connection. Electrical cables shall be run neatly and in cable ducts. All wiring shall be independently colour coded. Circuit breakers, contactors and overloads shall be fitted for all three phase motors.

The following components shall be incorporated, and factory fitted:

- Motor circuit breakers for all compressors

- Low level; terminal strip for field control wiring.

# Performance Schedule

| Unit Ref | Capacity | Energy Recovery | Model | Comments |
| --- | --- | --- | --- | --- |
|  | S/A (I/s) | O/A (I/s) | Ext Strat (Pa) | Heat (Kw) | Cool (Kw) | Reheat Coil (Kw) | Kw Recovered (Heat) | Kw Recovered (Cool) |  |  |
| Example | 3000 | 3000 | 250 | 30 | 70 | Plate | 65 | 60 | HTC3000 | Hot Water Coil for Heating |