# General

Air to Air Energy Recovery equipment shall be manufactured in Australia by Armcor Air Solutions www.armcor.com.au Ph. 1800 244 556. The units shall be factory assembled and internally wired, and fitted with large access doors allowing for service, cleaning and maintenance. The unit shall comply with the following design and manufacturing requirements and comply with the capacity requirement outlined in the attached performance schedule.

The manufacturer shall undertake a pre–commissioning check to ensure correct operation before the equipment leaves the factory.

Equipment shall be installed in a manner strictly in accordance with the manufacturers’ recommendations.

# Unit Construction

The unit shall be completely weatherproof and constructed according to the following requirements:

- The unit shall have a rigid galvanised steel base frame with crane lifting points

- The unit casing shall be constructed from 50mm double skin insulated Colorbond® panel

- The external panel shall have a minimum thermal rating of R1.5

- Units shall have large access doors to allow the internal parts to be accessed easily and removed for cleaning, servicing, maintenance, repair or replacement.

- Access doors shall be hinged and fitted with easy access opening mechanism.

- Access doors shall be fitted with rubber seals to eliminated air leakage

- Powdercoated aluminium profiles shall be used to join the casing panels, including H section, U section, base channel, door stop and angles

- All panels are to be fully sealed with non-perishable, mildew and mould resistant sealant and shall contain a VOC rating designed for extreme weather conditions.

# Heat Exchanger

## OPTION A [for Sensible Energy Recovery Applications]

- The air to air heat exchanger shall be a Rotary Heat Wheel with sensible media approved and tested by the equipment manufacturer

- The pressure drop and efficiencies shall be certified against Eurovent and/or ASHRAE standards at both summer and winter rating conditions

- Motors shall be suitable for variable speed drive

- Adjustable seals shall be provided between the rotor and the casing. Seals shall limit the leakage between supply and spill air to less than 5% of the supply air flow at 200Pa

- Rotary Wheel to be mounted in minimum 2.5mm welded steel frame with galvanised/painted finish to all surfaces

## OPTION B [for Enthalpy Energy Recovery Applications]

- The air to air heat exchanger shall be a Rotary Heat Wheel with enthalpy media approved and tested by the equipment manufacturer

- The pressure drop and efficiencies shall be certified against Eurovent and/or ASHRAE standards at both summer and winter rating conditions

- Motors shall be suitable for variable speed drive

- Adjustable seals shall be provided between the rotor and the casing. Seals shall limit the leakage between supply and spill air to less than 5% of the supply air flow at 200Pa

- Rotary Wheel to be mounted in minimum 2.5mm welded steel frame with galvanised/painted finish to all surfaces

# Fans

Fans used in the equipment shall be:

- Direct drive EC Backward Curved Centrifugal Plug Fans with Soft Start

- 0 – 10 Volt control input, to suit Variable Speed Drive (VSD) controller

- Thermal overload motor protection

- Performance to meet the required airflows and static pressures

# Filters

Filters shall be incorporated into the unit casing. Filters shall be easily removable through an access door for cleaning and replacement.

Filters shall be: [select option]

- 50mm V form disposable panel filters with F4 media.

- 600 deep bag filters.

- Dual filters - 600 deep bag filters and 50mm V form disposable panel pre-filters

# Electrical

The unit is to be fully factory wired with a control box for site connection. Electrical cables shall be run neatly and in cable ducts. All wiring shall be independently colour coded. Circuit breakers, contactors and overloads shall be fitted for all three phase motors.

The following components shall be incorporated and factory fitted:

[Select the appropriate options if required]

- Master switch/Circuit breakers

- 24 volt/240 volt contactors

# Coils (detail coil requirements if required)

Hot Water /Chilled Water Coils shall be constructed from copper tubes with bonded aluminum fins and have the following features:

- The velocity through the coils shall be designed at a maximum of 2.3 m/sec for low pressure drop and high efficiency

- Coils shall be pressure tested to 2200kPa (22 bar)

- The coils shall meet the required capacities outlined in the performance schedule

- Where cooling coils are included a stainless steel drain tray shall be installed to capture any condensation

# Performance Schedule

| Unit Ref | Capacity | Heat Exchanger | Fan Type | Model | Comments |
| --- | --- | --- | --- | --- | --- |
|  | S/A (I/s) | O/A (I/s) | Ext Strat (Pa) | Type | Kw Recovered (Cool) | Kw Recovered (Heat) |  |  |  |
| Example | 1200 | 1200 | 200 | Rotary | 18 | 30 | EC Plug | REM12000 | Unit fitted with 15kW Hot Water Coil |