# General

Ceiling Mounted Energy Recovery equipment shall be manufactured in Australia by Armcor Air   Solutions   www.armcor.com.au Ph. 1800 244 556. The units shall be factory assembled and internally wired, and fitted with large  access  doors  allowing for service, cleaning and maintenance. The unit shall comply with the following design and manufacturing requirements and comply with the capacity requirement outlined in the attached performance schedule.

The manufacturer shall undertake a pre–commissioning check to ensure correct operation before the equipment leaves the factory.

Equipment shall be installed in a manner strictly in accordance with the manufacturers’ recommendations.

# Unit Construction

The unit shall be completely weatherproof and constructed according to the following requirements:

- The unit casing shall be constructed from heavy duty galvanised steel with a minimum thickness of 1.0 mm

- Acoustic internal insulation shall be used with a minimum thickness of 25mm, having a density of not less than 36kg/m³, and a minimum thermal rating of R1.5

- Units shall have large access doors to allow the internal parts to be accessed easily and removed for cleaning, servicing, maintenance, repair or replacement

# Heat Exchanger

## OPTION A [for Sensible Energy Recovery Applications]

The heat exchanger shall be a Sensible plate heat exchanger with the following features:

- Crossflow or Counterflow Design so as to meet the required specifications

- Incorporate no moving parts

- Have entirely separate air paths for the supply and exhaust air to ensure no cross contamination

- Heat exchanger frame shall be formed from min 0.6mm coated steel or stabilized UPVC

## OPTION B [for Enthalpy Energy Recovery Applications]

The heat exchanger shall be an Enthalpy plate heat exchanger with the following features:

- Crossflow or Counterflow Design so as to meet the required specifications

- Incorporate no moving parts

- Heat exchanger frame shall be formed from min 0.6mm coated steel or stabilized UPVC

# Fans

Fans used in the equipment shall be:

- Direct drive EC Backward Curved Centrifugal Plug Fans with Soft Start

- 0 – 10 Volt control input, to suit Variable Speed Drive (VSD) controller

- Thermal overload motor protection

- Performance to meet the required airflows and static pressures

# Filters

Filters shall be incorporated into the unit casing and shall be easily removable through the access doors for cleaning and replacement.

Filters shall be:

- 10 mm panel filters with washable media (units up to 200l/sec)

- 50mm V form disposable panel filters with F4 media (units 300 – 1200 l/sec)

# Coils

A [Hot Water], [Chilled Water], [Direct Expansion], coil shall be fitted, constructed from copper tubes with bonded aluminum fins and have the following features:

- The velocity through the coils shall be designed at a maximum of 2.3 m/sec for low pressure drop and high efficiency

- Coils shall be pressure tested to 2200kPa (22 bar)

- The coils shall meet the required capacities outlined in the performance schedule

- A stainless steel drain tray shall be installed to capture any condensation

# Electrical

The unit is to be fully factory wired with a terminal box for site connection.

A factory fitted Integrated Variable Speed Drive (VSD) controller shall be included.

# Performance Schedule

| Unit Ref | Capacity | Heat Exchanger | Model | Comments |
| --- | --- | --- | --- | --- |
|  | S/A (I/s) | O/A (I/s) | Ext Strat (Pa) | Heat (Kw) | Cool (Kw) | Type | Cool | Heat |  |  |
| Example | 600 | 600 | 200 | - | 14 | Enthalphy Plate | 12.6 | 10.0 | XCC600 | Hot Water Coil Fitted |